LDWO Series Caravan Hot Water Oil-Fired Specification

Furnish and install, in compliance with manufacturer’s instructions and the rules and regulations of the authorities having jurisdiction.

Modular boilers shall have an A.H.R.I. burner capacity of ________GPH of  #2 fuel oil with a gross output of ________ BTUH and Net A.H.R.I. rating of _______ BTUH. Boiler shall be Slant/Fin Caravan Model _______ consisting of ____ modules or approved equal. Each module shall be clearly marked with the certification and approval symbols of ASME and A.H.R.I.
The heat exchanger for each module shall be wet base/wet back design fabricated from vertical cast iron sections, with an air separator cast into the front section. Dry base design boilers are not acceptable.  Water seal between sections shall be metal push nipples, gasket material is not acceptable. Each module shall be constructed in accordance with Section IV of the ASME boiler and pressure code for low-pressure boilers with a maximum working pressure of 100 PSIG. Each module shall be equipped with a temperature/pressure gauge, drain valve and ASME pressure relief valve with a set point _____ (30, 50, 75 or 100) PSI. The relief valve capacity shall exceed modules gross output, the installer shall pipe each relief valve to within 6 inches of the floor to a location that will show visible signs of discharge. All cast iron sections shall have a five-year manufacturer’s warranty.

Modules shall have a thermal efficiency of____ %. Each module shall have a swing open burner door to facilitate easy service. The oil burners shall be high pressure atomizing type high efficiency retention head that pass a quality control combustion test at the boiler manufacturers’ factory. A quality control sticker shall be applied to the burner tube to document this test. The installer shall complete a final combustion test during system start up. Oil supply to the modules shall be installed in accordance of boiler manufacturers, recommendations and code requirements shall be met.  Boiler system venting shall be installed as recommended by boiler manufacturer and code requirements met. Provision for combustion air must be made according to boiler manufacturer and code requirements. 
Each module shall allow complete cleaning of flue passages by removing top jacket and corrosion resistant aluminized steel flue collector. Cleaning must be performed from the top of each module and every thermal pin must be accessible for cleaning.
Modules shall be factory assembled and tested. A heavy gauge steel, insulated factory installed jacket shall enclose the cast iron heat exchanger. Each module shall have its own jacket to allow for unevenness in the boiler pad. One jacket for multiple modules is not acceptable.

Manufacturer shall provide, as standard equipment, a control manifold for installation in the supply piping to the system. The control header shall have three ½ inch tappings for the installation of a manual reset high limit, combination pressure/temperature gauge and system water temperature sensor. Installer shall provide, install and test manual reset high limit in boiler supply and manual reset low water cut-off. Code requirements must be satisfied. 

The heating plant floor load shall not exceed 125-pounds/square foot with factory headers and filled with water. For maintenance, the module design shall permit complete access to controls, burner, relief valve, temperature/pressure gauge and drain valve from the front of the modules.

Optional equipment:

Factory Headers- factory pre-fabricated welded steel supply and return water headers will be installed. Header shall be complete with flex joint fittings with inherent provision for expansion and contraction. Flex joint fittings shall have a temperature range for use up to 2500 F. Headers shall connect to 3 inch black pipe without use increaser or reducer. Factory supplied 1 ½ inches black pipe shall connect each module to supply and return headers.

(List step control)

(List factory representative start-up supervision)

