Galaxy hot water Series

Furnish and install, as shown on the plans, ____(Qty) Galaxy model GG______ gas-fired hot water boiler(s). These boilers shall have a CSA design certified input of _____Btuh, D.O.E. heating capacity of _____Btuh and a Net I=B=R rating of ______Btuh. The A.F.U.E. efficiency shall be ___%. 

Electrical service shall be 115 volt 60 hertz 1 phase. Boiler(s) shall be CSA designed certified. Factory supplied rating plate shall have CSA designed certified symbol and ASME “H” stamp. If required, installer shall provide low water cut-off, additional hi-limit control and any additional items to satisfy local boiler code requirements.

Boiler(s) heat exchanger(s) shall be constructed of cast iron sections with casting assembly being clearly marked with the ASME symbol. Sections shall be assembled in accordance with ASME requirements using metal push nipple seals between the sections that will provide a permanent heat and chemical resistant seal, gasket or rubber seals are not acceptable. Maximum ASME working pressure shall be 100 PSI. Each section shall be hydrostatically tested at the foundry and casting assemblies hydrostatically tested on final assembly line in accordance with ASME Code. Casting assemblies shall be hydrostatically tested at the factory a third time to ensure quality. Boiler flues shall have cast iron thermal pins with a pattern that ensures uniform heat transfer.
Factory supplied A.S.M.E safety relief valve and pressure/temperature gauge must be supplied. Safety relief valve shall be rated at 30 P.S.I. 

Boiler(s) shall be manufactured for use in a vent category I (chimney vented) application. 
Boiler(s) flue collector shall be manufactures out of heavy gauge aluminized steel. The boiler base assembly shall be constructed of heavy gauge aluminized steel with thick refractory insulation on the inside. 
(Electronic Ignition- Ignition shall be accomplished through intermittent pilot spark ignition; hot surface ignition is not acceptable. Pilot shall be burner mounted to facilitate accurate location of pilot for smooth ignition of main burner.)
or
(Standing Pilot- Ignition shall be accomplished through standing pilot ignition. Pilot shall be burner mounted to facilitate accurate location of pilot for smooth ignition of main burners.)  
Burners shall be one piece stainless steel construction, aluminized steel is not acceptable. Each burner shall have an adjustable air shutter used to adjust the combustion as required. Burners without adjustable air shutters are not acceptable.
Boiler jacket shall be, durable painted steel, insulated and factory installed.

Installer shall install and test fire boiler(s) in accordance with manufacturer’s installation instructions and local authority requirements.

